## Recalculation table
Radiant convector EXACT at temperature gradient 75/65/20 °C | [6 empty] | ISAN Radiátory, s.r.o. Poříčí 26, 678 33 Blansko Czech Republic, www.isan.cz
ORIENTATION RECALCULATION OF THE RADIANT CONVECTORS HEATING OUTPUT
T1>T2>Ti
Type |  |  | Input: |  | Output: |  | Room:
Q[W] 75/65/20°C (ΔT=50°C) | [5 empty] | Q[W] 75/65/20°C (ΔT=50°C)
Length [mm] | Heating output [W] |  |  |  |  | Length [mm] | Heating output [W]
| Height [mm] | [5 empty] | Height [mm] |  |  |  | min | 1 | max | 1
| 70 | 140 | 210 | 280 |  |  | 70 | 140 | 210 | 280
400 | 134.2082 | 209.6458 | 273.1011 | 330.2703 |  | 400 | 134.2082 | 209.6458 | 273.1011 | 330.2703 | 1 | 1 | 1 | 1
500 | 167.7602 | 262.0573 | 341.3763 | 412.8379 |  | 500 | 167.7602 | 262.0573 | 341.3763 | 412.8379 | 1 | 1 | 1 | 1
600 | 201.3123 | 314.4688 | 409.6516 | 495.4055 |  | 600 | 201.3123 | 314.4688 | 409.6516 | 495.4055 | 1 | 1 | 1 | 1
700 | 234.8643 | 366.8802 | 477.9269 | 577.9731 |  | 700 | 234.8643 | 366.8802 | 477.9269 | 577.9731 | 1 | 1 | 1 | 1
800 | 268.4164 | 419.2917 | 546.2022 | 660.5407 |  | 800 | 268.4164 | 419.2917 | 546.2022 | 660.5407 | 1 | 1 | 1 | 1
900 | 301.9684 | 471.7031 | 614.4774 | 743.1082 |  | 900 | 301.9684 | 471.7031 | 614.4774 | 743.1082 | 1 | 1 | 1 | 1
1000 | 335.5205 | 524.1146 | 682.7527 | 825.6758 |  | 1000 | 335.5205 | 524.1146 | 682.7527 | 825.6758 | 1 | 1 | 1 | 1
1100 | 369.0725 | 576.526 | 751.028 | 908.2434 |  | 1100 | 369.0725 | 576.526 | 751.028 | 908.2434 | 1 | 1 | 1 | 1
1200 | 402.6246 | 628.9375 | 819.3032 | 990.811 |  | 1200 | 402.6246 | 628.9375 | 819.3032 | 990.811 | 1 | 1 | 1 | 1
1300 | 436.1766 | 681.349 | 887.5785 | 1073.3786 |  | 1300 | 436.1766 | 681.349 | 887.5785 | 1073.3786 | 1 | 1 | 1 | 1
1400 | 469.7287 | 733.7604 | 955.8538 | 1155.9461 |  | 1400 | 469.7287 | 733.7604 | 955.8538 | 1155.9461 | 1 | 1 | 1 | 1
1500 | 503.2807 | 786.1719 | 1024.129 | 1238.5137 |  | 1500 | 503.2807 | 786.1719 | 1024.129 | 1238.5137 | 1 | 1 | 1 | 1
1600 | 536.8328 | 838.5833 | 1092.4043 | 1321.0813 |  | 1600 | 536.8328 | 838.5833 | 1092.4043 | 1321.0813 | 1 | 1 | 1 | 1
1700 | 570.3848 | 890.9948 | 1160.6796 | 1403.6489 |  | 1700 | 570.3848 | 890.9948 | 1160.6796 | 1403.6489 | 1 | 1 | 1 | 1
1800 | 603.9369 | 943.4063 | 1228.9549 | 1486.2165 |  | 1800 | 603.9369 | 943.4063 | 1228.9549 | 1486.2165 | 1 | 1 | 1 | 1
1900 | 637.4889 | 995.8177 | 1297.2301 | 1568.784 |  | 1900 | 637.4889 | 995.8177 | 1297.2301 | 1568.784 | 1 | 1 | 1 | 1
2000 | 671.041 | 1048.2292 | 1365.5054 | 1651.3516 |  | 2000 | 671.041 | 1048.2292 | 1365.5054 | 1651.3516 | 1 | 1 | 1 | 1
2100 | 704.593 | 1100.6406 | 1433.7807 | 1733.9192 |  | 2100 | 704.593 | 1100.6406 | 1433.7807 | 1733.9192 | 1 | 1 | 1 | 1
2200 | 738.1451 | 1153.0521 | 1502.0559 | 1816.4868 |  | 2200 | 738.1451 | 1153.0521 | 1502.0559 | 1816.4868 | 1 | 1 | 1 | 1
2300 | 771.6971 | 1205.4636 | 1570.3312 | 1899.0544 |  | 2300 | 771.6971 | 1205.4636 | 1570.3312 | 1899.0544 | 1 | 1 | 1 | 1
2400 | 805.2492 | 1257.875 | 1638.6065 | 1981.622 |  | 2400 | 805.2492 | 1257.875 | 1638.6065 | 1981.622 | 1 | 1 | 1 | 1
2500 | 838.8012 | 1310.2865 | 1706.8817 | 2064.1895 |  | 2500 | 838.8012 | 1310.2865 | 1706.8817 | 2064.1895 | 1 | 1 | 1 | 1
2600 | 872.3533 | 1362.6979 | 1775.157 | 2146.7571 |  | 2600 | 872.3533 | 1362.6979 | 1775.157 | 2146.7571 | 1 | 1 | 1 | 1
2700 | 905.9053 | 1415.1094 | 1843.4323 | 2229.3247 |  | 2700 | 905.9053 | 1415.1094 | 1843.4323 | 2229.3247 | 1 | 1 | 1 | 1
2800 | 939.4574 | 1467.5208 | 1911.7075 | 2311.8923 |  | 2800 | 939.4574 | 1467.5208 | 1911.7075 | 2311.8923 | 1 | 1 | 1 | 1
2900 | 973.0094 | 1519.9323 | 1979.9828 | 2394.4599 |  | 2900 | 973.0094 | 1519.9323 | 1979.9828 | 2394.4599 | 1 | 1 | 1 | 1
3000 | 1006.5615 | 1572.3438 | 2048.2581 | 2477.0274 |  | 3000 | 1006.5615 | 1572.3438 | 2048.2581 | 2477.0274 | 1 | 1 | 1 | 1
3100 | 1040.1135 | 1624.7552 | 2116.5334 | 2559.595 |  | 3100 | 1040.1135 | 1624.7552 | 2116.5334 | 2559.595 | 1 | 1 | 1 | 1
3200 | 1073.6656 | 1677.1667 | 2184.8086 | 2642.1626 |  | 3200 | 1073.6656 | 1677.1667 | 2184.8086 | 2642.1626 | 1 | 1 | 1 | 1
3300 | 1107.2176 | 1729.5781 | 2253.0839 | 2724.7302 |  | 3300 | 1107.2176 | 1729.5781 | 2253.0839 | 2724.7302 | 1 | 1 | 1 | 1
3400 | 1140.7696 | 1781.9896 | 2321.3592 | 2807.2978 |  | 3400 | 1140.7696 | 1781.9896 | 2321.3592 | 2807.2978 | 1 | 1 | 1 | 1
3500 | 1174.3217 | 1834.4011 | 2389.6344 | 2889.8653 |  | 3500 | 1174.3217 | 1834.4011 | 2389.6344 | 2889.8653 | 1 | 1 | 1 | 1
3600 | 1207.8737 | 1886.8125 | 2457.9097 | 2972.4329 |  | 3600 | 1207.8737 | 1886.8125 | 2457.9097 | 2972.4329 | 1 | 1 | 1 | 1
3700 | 1241.4258 | 1939.224 | 2526.185 | 3055.0005 |  | 3700 | 1241.4258 | 1939.224 | 2526.185 | 3055.0005 | 1 | 1 | 1 | 1
3800 | 1274.9778 | 1991.6354 | 2594.4602 | 3137.5681 |  | 3800 | 1274.9778 | 1991.6354 | 2594.4602 | 3137.5681 | 1 | 1 | 1 | 1
3900 | 1308.5299 | 2044.0469 | 2662.7355 | 3220.1357 |  | 3900 | 1308.5299 | 2044.0469 | 2662.7355 | 3220.1357 | 1 | 1 | 1 | 1
4000 | 1342.0819 | 2096.4584 | 2731.0108 | 3302.7033 |  | 4000 | 1342.0819 | 2096.4584 | 2731.0108 | 3302.7033 | 1 | 1 | 1 | 1
4100 | 1375.634 | 2148.8698 | 2799.286 | 3385.2708 |  | 4100 | 1375.634 | 2148.8698 | 2799.286 | 3385.2708 | 1 | 1 | 1 | 1
4200 | 1409.186 | 2201.2813 | 2867.5613 | 3467.8384 |  | 4200 | 1409.186 | 2201.2813 | 2867.5613 | 3467.8384 | 1 | 1 | 1 | 1
4300 | 1442.7381 | 2253.6927 | 2935.8366 | 3550.406 |  | 4300 | 1442.7381 | 2253.6927 | 2935.8366 | 3550.406 | 1 | 1 | 1 | 1
4400 | 1476.2901 | 2306.1042 | 3004.1119 | 3632.9736 |  | 4400 | 1476.2901 | 2306.1042 | 3004.1119 | 3632.9736 | 1 | 1 | 1 | 1
4500 | 1509.8422 | 2358.5156 | 3072.3871 | 3715.5412 |  | 4500 | 1509.8422 | 2358.5156 | 3072.3871 | 3715.5412 | 1 | 1 | 1 | 1
4600 | 1543.3942 | 2410.9271 | 3140.6624 | 3798.1087 |  | 4600 | 1543.3942 | 2410.9271 | 3140.6624 | 3798.1087 | 1 | 1 | 1 | 1
4700 | 1576.9463 | 2463.3386 | 3208.9377 | 3880.6763 |  | 4700 | 1576.9463 | 2463.3386 | 3208.9377 | 3880.6763 | 1 | 1 | 1 | 1
4800 | 1610.4983 | 2515.75 | 3277.2129 | 3963.2439 |  | 4800 | 1610.4983 | 2515.75 | 3277.2129 | 3963.2439 | 1 | 1 | 1 | 1
4900 | 1644.0504 | 2568.1615 | 3345.4882 | 4045.8115 |  | 4900 | 1644.0504 | 2568.1615 | 3345.4882 | 4045.8115 | 1 | 1 | 1 | 1
5000 | 1677.6024 | 2620.5729 | 3413.7635 | 4128.3791 |  | 5000 | 1677.6024 | 2620.5729 | 3413.7635 | 4128.3791 | 1 | 1 | 1 | 1
5100 | 1711.1545 | 2672.9844 | 3482.0387 | 4210.9466 |  | 5100 | 1711.1545 | 2672.9844 | 3482.0387 | 4210.9466 | 1 | 1 | 1 | 1
5200 | 1744.7065 | 2725.3959 | 3550.314 | 4293.5142 |  | 5200 | 1744.7065 | 2725.3959 | 3550.314 | 4293.5142 | 1 | 1 | 1 | 1
5300 | 1778.2586 | 2777.8073 | 3618.5893 | 4376.0818 |  | 5300 | 1778.2586 | 2777.8073 | 3618.5893 | 4376.0818 | 1 | 1 | 1 | 1
5400 | 1811.8106 | 2830.2188 | 3686.8646 | 4458.6494 |  | 5400 | 1811.8106 | 2830.2188 | 3686.8646 | 4458.6494 | 1 | 1 | 1 | 1
5500 | 1845.3627 | 2882.6302 | 3755.1398 | 4541.217 |  | 5500 | 1845.3627 | 2882.6302 | 3755.1398 | 4541.217 | 1 | 1 | 1 | 1
5600 | 1878.9147 | 2935.0417 | 3823.4151 | 4623.7846 |  | 5600 | 1878.9147 | 2935.0417 | 3823.4151 | 4623.7846 | 1 | 1 | 1 | 1
5700 | 1912.4668 | 2987.4532 | 3891.6904 | 4706.3521 |  | 5700 | 1912.4668 | 2987.4532 | 3891.6904 | 4706.3521 | 1 | 1 | 1 | 1
5800 | 1946.0188 | 3039.8646 | 3959.9656 | 4788.9197 |  | 5800 | 1946.0188 | 3039.8646 | 3959.9656 | 4788.9197 | 1 | 1 | 1 | 1
5900 | 1979.5709 | 3092.2761 | 4028.2409 | 4871.4873 |  | 5900 | 1979.5709 | 3092.2761 | 4028.2409 | 4871.4873 | 1 | 1 | 1 | 1
6000 | 2013.1229 | 3144.6875 | 4096.5162 | 4954.0549 |  | 6000 | 2013.1229 | 3144.6875 | 4096.5162 | 4954.0549 | 1 | 1 | 1 | 1

## Nová data tabulka Exact (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Model | NOVÁ DATA SZU W/m |  | 75 | 65 | 20 | Teplota vstupní vody | 75 | T1 | podmínka |  | výsledek | hledaná hodnota -5% až + 15%
K21 | 335.5205 | 524.1146 | 682.7527 | 825.6758 |  | 1.2943 | 1.2965 | 1.2986 | 1.3008 | EXACT | ΔT 50K | Exp. (n)* | 16 | 7 | 9 | Teploty výstupní vody | 65 | T2 | (T2-Ti)/(T1-Ti) | <0,7 | (T1-T2)/(ln((T1-Ti)/(T2-Ti)) | Výkon*(Výsledek/50)^Teplotní exponent
K22 | 435.4462 | 692.69 | 900.1577 | 1076.815 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K21-070 | 335.5205 | 1.2943 | 90 | 71 | 28 | Teplota místnosti | 20 | Ti |  | >=0,7 | (T1+T2)/2-Ti | Výkon*(Výsledek/50)^Teplotní exponent
K22W | 435.4462 | 692.69 | 900.1577 | 1076.815 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K21-140 | 524.1146 | 1.2965 | 89 | 70 | 27 | kontrola teplotní spád | 70 |  | 0.81818 |  | 50
K32 | 577.9101 | 902.75 | 1175.9929 | 1422.1677 |  | 1.2943 | 1.2965 | 1.2986 | 1.3008 | K21-210 | 682.7527 | 1.2986 | 88 | 69 | 26 | kontrola hmotnostní průtok | 1
K33 | 666.386 | 1060.0595 | 1377.5583 | 1647.9061 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K21-280 | 825.6758 | 1.3008 | 87 | 68 | 25 |  | 682.7527 | 50
K33W | 666.386 | 1060.0595 | 1377.5583 | 1647.9061 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K22(W)-070 | 435.4462 | 1.3049 | 86 | 67 | 24 |  | 682.7527
K43 | 808.5695 | 1263.0616 | 1645.363 | 1989.7928 |  | 1.2943 | 1.2965 | 1.2986 | 1.3008 | K22(W)-140 | 692.69 | 1.299 | 85 | 66 | 23 |  | 1.2986
K44 | 890.5888 | 1416.7122 | 1841.032 | 2202.3372 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K22(W)-210 | 900.1577 | 1.2932 | 84 | 65 | 22
K45 | 890.5888 | 1416.7122 | 1841.032 | 2202.3372 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K22(W)-280 | 1076.815 | 1.2873 | 83 | 64 | 21
K54 | 1028.0512 | 1605.9128 | 2091.9877 | 2529.9111 |  | 1.2943 | 1.2965 | 1.2986 | 1.3008 | K32-070 | 577.9101 | 1.2943 | 82 | 63 | 20
K55 | 1110.0534 | 1765.8275 | 2294.711 | 2745.0513 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K32-140 | 902.75 | 1.2965 | 81 | 62 | 19
K55W | 1110.0534 | 1765.8275 | 2294.711 | 2745.0513 |  | 1.3049 | 1.299 | 1.2932 | 1.2873 | K32-210 | 1175.9929 | 1.2986 | 80 | 61 | 18
1 | [9 empty] | K32-280 | 1422.1677 | 1.3008 | 79 | 60 | 17
K21 | [5 empty] | 1.2966 |  |  |  | K33(W)-070 | 666.386 | 1.3049 | 78 | 59 | 16
[6 empty] | 1.2976 |  |  |  | K33(W)-140 | 1060.0595 | 1.299 | 77 | 58 | 15
[10 empty] | K33(W)-210 | 1377.5583 | 1.2932 | 76 | 57
[10 empty] | K33(W)-280 | 1647.9061 | 1.2873 | 75 | 56
[10 empty] | K43-070 | 808.5695 | 1.2943 | 74 | 55
[10 empty] | K43-140 | 1263.0616 | 1.2965 | 73 | 54
[10 empty] | K43-210 | 1645.363 | 1.2986 | 72 | 53
[10 empty] | K43-280 | 1989.7928 | 1.3008 | 71 | 52
[10 empty] | K44(W)-070 | 890.5888 | 1.3049 | 70 | 51
[10 empty] | K44(W)-140 | 1416.7122 | 1.299 | 69 | 50
[10 empty] | K44(W)-210 | 1841.032 | 1.2932 | 68 | 49
[10 empty] | K44(W)-280 | 2202.3372 | 1.2873 | 67 | 48
[10 empty] | K54-070 | 1028.0512 | 1.2943 | 66 | 47
[10 empty] | K54-140 | 1605.9128 | 1.2965 | 65 | 46
[10 empty] | K54-210 | 2091.9877 | 1.2986 | 64 | 45
[10 empty] | K54-280 | 2529.9111 | 1.3008 | 63 | 44
[10 empty] | K55(W)-070 | 1110.0534 | 1.3049 | 62 | 43
[10 empty] | K55(W)-140 | 1765.8275 | 1.299 | 61 | 42
[10 empty] | K55(W)-210 | 2294.711 | 1.2932 | 60 | 41
[10 empty] | K55(W)-280 | 2745.0513 | 1.2873 | 59 | 40
[13 empty] | 58 | 39
[13 empty] | 57 | 38
[13 empty] | 56 | 37
[13 empty] | 55 | 36
[13 empty] | 54 | 35
[13 empty] | 53 | 34
[13 empty] | 52 | 33
[13 empty] | 51 | 32
[13 empty] | 50 | 31
[13 empty] | 49 | 30
48
47
46
45
44
43
42
41
40
39
38
37
36
35